FLOOR TEST

|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SN | Location | Parent Location | Facility Area | Distance from previous test location (m) | Nominal Voltage to Earth of System (V) | Applied Test Voltage (V) | Measured Output Current (mA) | EffectiveResistance | Result |
| 1 | Point-1 | Main Floor | LT Panel Room | 1.20 | 230 | 230 | 3.10 | 74.19 | pass |
| 2 | Point-2 | Wall -1 | LT Panel Room | 0.90 | 230 | 230 | 5.60 | 41.07 | fail |
| 3 | Point-3 | Main Floor | Office Room | 1.10 | 230 | 230 | 3.20 | 71.88 | pass |



