|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SN | Device ID | Device Name | Location | Voltage Rating (V) | Fuse Rating (A) | Visual Inspection | Earth Continuity (?) | Insulation Resistance (M?) | Polarity Test | Leakage (mA) | Functional Check | Overall Result |
| 1 | A1024 | Hand Drill | Workshop | 240 | 10 | OK | 0.1 | 1 | OK | 0.1 | OK | PASS |
| 2 | B1024 | Hot Blower | Electrical Panel Room | 240 | 10 | Not OK | 0.2 | 2 | OK | 0.1 | OK | FAIL |
| 3 | C1024 | Angle Grinder | Workshop | 240 | 10 | OK | 0.15 | 2 | Not OK | 0.05 | OK | PASS |

