

TESTING REPORT

FLOOR-RESISTANCE TEST


|  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SN | Location | Parent Location | Facility Area | Distance from previous test location (m) | Nominal Voltage to Earth of System (V) | Applied Test Voltage (V) | Measured Output Current (mA) | EffectiveResistance | Result |
| 1 | Point-1 | Main Floor | LT Panel Room | 1.20 | 230 | 230 | 3.10 | 74.19 | Pass |
| 2 | Point-2 | Wall -1 | LT Panel Room | 0.90 | 230 | 230 | 5.60 | 41.07 | Fail |
| 3 | Point-3 | Main Floor | Office Room | 1.10 | 230 | 230 | 3.20 | 71.88 | Pass |






INSULATION TEST


|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SN | Location | Parent Location | Upstream Device Name | No. Poles | SPD Applicable | Earthing System | Nominal Circuit Voltage | Measurement Terminals | Test Voltage (V) | Conductor Type | Conductor Size | Insulation Type | Insulation Resistance (MΩ) | Result |
| 1 | MCB-1 | LV Board | MCCB-2 | Single | No | TNS | 230 | L1-E | 500 | Copper | 6.0 | PVC | 10.0 | Pass |
| 2 | MCB-4 | Feeder-2 | MCCB-1 | Single | No | TNS | 230 | L1-E | 500 | Aluminium | 4.0 | XLPE | 1.88 | Pass |
| 3 | MCB-6 | Feeder-3 | MCCB-1 | Three | No | TNS | 415 | L1L2L3-E | 500 | Copper | 10.0 | XLPE | 0.8 | Pass |
| 4 | MCB-6 | Feeder-3 | MCCB-1 | Three | No | TNC | 415 | L1-N | 500 | Copper | 10.0 | XLPE | 2.2 | Fail |
| 5 | MCB-6 | Feeder-3 | MCCB-1 | Three | No | TNC | 415 | L2-N | 500 | Copper | 10.0 | XLPE | 3.6 | Pass |
| 6 | MCB-6 | Feeder-3 | MCCB-1 | Three | No | TNC | 415 | L3-N | 500 | Copper | 10.0 | XLPE | 0.5 | Pass |
| 7 | Socket-2 | LV Board | MCB-6 | Single | Yes | TNS | 230 | L1-E | 500 | Aluminium | 2.5 | PVC | 0.9 | Fail |
| 8 | HT Breaker-1 | HT Panel | Main HT Incomer | Three | No | TNS | 11000 | L1L2L3-E | 1000 | Aluminium | 400.0 | XLPE | 50.0 | Fail |






PHASE SEQUENCE TEST


|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SN | Location | Location Type | Parent Location | Facility Area | V-L1-L2 | V-L2-L3 | V-L3-L1 | V-L1-N | V-L2-N | V-L3-N | Phase Sequence | Result |
| 1 | SFU-1 | SFU | DB-2 | Electrical Panel Room | 415 | 412 | 414 | 240 | 238 | 239 | RYB | CLOCKWISE |
| 2 | MCCB-1 | MCCB | Main Panel | Electrical Panel Room | 420 | 417 | 419 | 242 | 241 | 242 | RBY | ANTICLOCKWISE |






POLARITY TEST


|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SN | Location | Parent Location | Facility Area | Device Type | Line to Neutral Voltage (V) | Type of Supply | Polarity Reference | Result |
| 1 | MCB-1 | DB-1 | Offiice Room | MCB | 230 | AC | Cores | OK |
| 2 | DC MCB-2 | UPS | Electrical Panel Room | MCB | 220 | DC | Device | REVERSE |
| 3 | RCB-2 | DB-2 | Workshop | RCCB | 235 | AC | Cores | REVERSE |






VOLTAGE DROP TEST


|  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SN | Circuit Route[FROM] | Circuit Route[TO] | Measured Voltage (V, L-N)[FROM] | Measured Voltage (V, L-N)[TO] | Nominal Circuit Voltage (V AC) | Type of Installation Supply System | Purpose of Supply | Cable Length (m) | Conductor Type | Insulation Type | Calculated Voltage Drop (V) | Voltage Drop % | Result |
| 1 | Main ACB | Light | 220 | 215 | 230 | Public | Lighting | 160 | Cu | PVC | 5 | 2.27 | Pass |
| 2 | Main ACB | Computer Station | 225 | 201 | 230 | Private | Other | 80 | Al | XLPE | 24 | 10.67 | Fail |






Residual Current Device Test

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Location | Parent Location | Facility Area | Type of Voltage Waveform | Type of Earthing System | Nominal Line to Earth Voltage (V) | Nominal Current Rating(A) | Rated Residual Operating Current,I?n (mA) | Type | Trip curve type | No. of Poles | Test Current (mA) | Trip Current (mA) | Trip Time (ms) | Device Tripped | Result |
| RCCB-1 | LT Panel | LT Panel Room | AC | TN | 230 | 100 | 100 | A | Standard | 2 | 50 | - | - | No | Pass |
| RCCB-1 | LT Panel | LT Panel Room | AC | TN | 230 | 100 | 100 | A | Standard | 3 | 100 | 101 | 151 | Yes | Pass |
| RCCB-1 | LT Panel | LT Panel Room | AC | TN | 230 | 100 | 100 | A | Standard | 4 | 200 | 201 | 102 | Yes | Pass |
| RCCB-1 | LT Panel | LT Panel Room | AC | TN | 230 | 100 | 100 | A | Standard | 5 | 500 | 501 | 75 | Yes | Pass |
| RCCB - 2 | DB | Workshop Area | AC | TN | 228 | 63 | 100 | AC | General | 2 | 50 | 50 | 90 | Yes | Fail |
| RCCB - 2 | DB | Workshop Area | AC | TN | 229 | 63 | 100 | AC | General | 3 | 100 | 102 | 352 | Yes | Fail |
| RCCB - 2 | DB | Workshop Area | AC | TN | 230 | 63 | 100 | AC | General | 4 | 200 | 202 | 156 | Yes | Fail |
| RCCB - 2 | DB | Workshop Area | AC | TN | 231 | 63 | 100 | AC | General | 5 | 500 | 502 | 57 | Yes | Fail |
| RCCB-1 | LT Panel | LT Panel Room | AC | TN | 230 | 100 | 100 | A | Standard | 2 | 50 | 502 | 57 | Yes | Fail |
| RCCB-1 | LT Panel | LT Panel Room | AC | TN | 230 | 100 | 100 | A | Standard | 3 | 100 | 101 | 1500 | Yes | Fail |
| RCCB-1 | LT Panel | LT Panel Room | AC | TN | 230 | 100 | 100 | A | Standard | 4 | 200 | 201 | 102 | No | Fail |
| RCCB-1 | LT Panel | LT Panel Room | AC | TN | 230 | 100 | 100 | A | Standard | 5 | 500 | 501 | 1000 | Yes | Fail |
| RCCB - 2 | DB | Workshop Area | AC | TN | 228 | 63 | 100 | AC | General | 2 | 50 | - | - | No | Pass |
| RCCB - 2 | DB | Workshop Area | AC | TN | 229 | 63 | 100 | AC | General | 3 | 100 | 102 | 250 | Yes | Pass |
| RCCB - 2 | DB | Workshop Area | AC | TN | 230 | 63 | 100 | AC | General | 4 | 200 | 202 | 140 | Yes | Pass |
| RCCB - 2 | DB | Workshop Area | AC | TN | 231 | 63 | 100 | AC | General | 5 | 500 | 502 | 33 | Yes | Pass |





EARTH PIT RESISTANCE TEST

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SN | Earth Pit Name | Earth Pit Location | No. of Parallel Electrodes | Earthing Application | Type of Earthing | Earth Electrode Depth | Nearest Electrode Distance | Measured Earth Resistance - Individual | Electrode Distance Ratio | Calculated Earth Resistance - Individual (Ω) | Result | Remark |
| 1 | Earth Pit -1 | Transformer Area | 2 | Body Earth | Chemical Electrode Earthing | 3 | 2 | 1.9 | 0.67 | 3.8 | PASS | Test Electrodes are not properly placed |
| 2 | Earth Pit -2 | Outdoor Area | 2 | Body Earth & Protection | Chemical Electrode Earthing | 3 | 3 | 3.6 | 1.0 | 7.2 | FAIL | Test Electrodes are properly placed |
| 3 | Earth Pit -3 | Transformer Area | 2 | Body Earth | Chemical Electrode Earthing | 3 | 2 | 2.1 | 0.67 | 4.2 | FAIL | Test Electrodes are not properly placed |
| 4 | Earth Pit -4 | Outdoor Area | 2 | Body Earth & Protection | Chemical Electrode Earthing | 3 | 3 | 1.5 | 1.0 | 3.0 | PASS | Test Electrodes are properly placed |

