Three Phase Symmetry Test

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sr. No. | Location Name | Parent Location | Facility Area | Rated Line Voltage (V) | Average Line Voltage (V) | Average Phase Voltage (V) | Voltage Unbalance % | Voltage Result | Rated Phase Current (A) | Average Phase Current (A) | Current Unbalance % | Current Result | Voltage-NE (V) | NEV Result | Zero Sum Current (mA) | ZeroSum Result |
| 1 | Main Incomer | MLTP | Electrical Panel Room | 415 | 418.33 | 230.0 | 43.82 | FAIL | 630 | 465.0 | 4.78 | PASS | 3 | FAIL | 105 | PASS |
| 2 | Main Incomer | MLTP | Electrical Panel Room | 450 | 420.0 | 252.0 | 43.65 | FAIL | 670 | 553.0 | 4.76 | PASS | 2 | PASS | 150 | FAIL |

